## INSTRUCTIONS
QUICK START GUIDE ¦ PE80 Gas Network Hydraulic Solver Input Template
STEP 1 MATERIALS (read only)
› | The MATERIALS sheet is pre-filled. Do not modify the PE80 row.
› | If your network has steel segments, update the roughness value for Steel_aged based on pipe condition survey.
› | The ID dimension table (lower half) is for reference all PE80 IDs are auto-calculated in PIPES using OD and SDR.
STEP 2 POPULATE NODES SHEET
› | Add one row per node. Every tee, every PRS, every meter station = one row.
› | Set Node_Type using the dropdown: source / junction / offtake.
› | SOURCE nodes: fill Known_P_kPa_g only (e.g. 4 bar(g) after regulator). Leave Demand blank.
› | OFFTAKE nodes: fill Demand_Sm3h and Diversity_Factor. Leave Known_P blank.
› | JUNCTION nodes: Demand = 0, Known_P blank, DF = 1.0.
› | Eff_Demand (column J) is a formula =G*I do not overwrite it.
› | Fill X_Coord and Y_Coord if you have GIS data used for pressure maps.
STEP 3 POPULATE PIPES SHEET
› | Add one row per pipe segment. A 'segment' = a pipe between two nodes.
› | From_Node and To_Node must exactly match Node_IDs (case-sensitive).
› | Length_m = physical route length, NOT straight-line map distance.
› | OD_mm = outside diameter in mm (standard PE80 sizes: 63, 90, 125, 160, 200, 250 mm).
› | SDR = 11 for this 4 bar(g) PE80 network (use dropdown).
› | ID_mm (column G) and Roughness_mm (column I) are FORMULAS do not overwrite.
› | Columns L, M, N are solver-ready unit conversions do not modify.
› | Set Status = 'closed' for any valve-isolated section to exclude from solve.
STEP 4 RUN VALIDATION SHEET
› | Go to VALIDATION sheet and check all rows show ✓ PASS.
› | The final row (V20) shows the overall result ALL checks must pass before running Python.
› | Fix any ✗ FAIL items before proceeding.
› | Pay attention to V01/V02 node name mismatches are the most common error.
STEP 5 EXPORT TO PYTHON SOLVER
› | The Python solver reads this file with: pd.read_excel('network.xlsx', sheet_name='NODES')
› | And: pd.read_excel('network.xlsx', sheet_name='PIPES')
› | Solver uses columns: Node_ID, Node_Type, Known_P_kPa_g, Eff_Demand_Sm3h, Elevation_m
› | Solver uses columns: Pipe_ID, From_Node, To_Node, Length_m_SI, ID_m_SI, Rough_m_SI, Status
› | Only pipes with Status = 'open' are included in the solve.
› | Converged pressures and flows are written back to a RESULTS sheet automatically.

## NODES
GAS DISTRIBUTION NETWORK NODE TABLE ¦ PE80 · 4 bar(g) · SI Units
Node_ID | Node_Type | Name | Zone | Elevation_m | Known_P_kPa_g | Demand_Sm3h | Demand_Type | Diversity_Factor | Eff_Demand_Sm3h | Min_P_kPa_g | X_Coord | Y_Coord | LEGEND
N001 | source | PRS1 | Zone_A | 0 | 400 | [5 empty] | 338450 | 3318200 | Source Node | Fixed pressure boundary Known_P_kPa filled
N002 | junction | TEE1 | Zone_A | 0 |  | 0 |  | 1 |  |  | 338720 | 3318200 | Offtake Node | Known demand Demand_Sm3h + DF filled
N003 | junction | TEE2 | Zone_A | 0 |  | 0 |  | 1 |  |  | 338720 | 3318480 | Junction Node | Zero demand solver computes pressure
N004 | junction | TEE3 | Zone_B | 0 |  | 0 |  | 1 |  |  | 338720 | 3317920 | Known_P cell | Fixed boundary pressure (sources only)
N005 | offtake | Client1 | Zone_A | 0 |  | 1000 | industrial | 1 |  | 390 | 338980 | 3318580 | Demand cell | Raw peak demand (offtakes only)
N006 | offtake | Client2 | Zone_A | 0 |  | 750 | industrial | 1 |  | 390 | 338980 | 3318380 | Div. Factor | Simultaneity factor 0–1
N007 | offtake | Client3 | Zone_B | 0 |  | 500 | industrial | 1 |  | 390 | 338980 | 3317920 | Eff_Demand | Formula = Demand × DF → passed to solver
N008 | offtake | Client4 | Zone_B | 0 |  | 600 | industrial | 1 |  | 390 | 338980 | 3317780 | ⚠ ERROR | Red = data entry conflict fix before running solver
N009 | source | PRS2 | Zone_B | 0 | 400 | [5 empty] | 338200 | 3317600
N010 | offtake | Client5 | Zone_B | 0 |  | 210 | industrial | 1 |  | 390 | 338980 | 3317620
Note on A2: Unique node identifier Format: N001, N002... Used as primary key in PIPES table
Note on B2: Dropdown: source / junction / offtake • source = fixed pressure boundary • junction = zero demand, pressure unknown • offtake = known demand, pressure unknown
Note on C2: Descriptive label e.g. 'PRS Maadi', 'Block 7 Meters' For human reference only
Note on D2: District or pressure area e.g. Zone_A, Zone_B Used for grouping in reports
Note on E2: Ground elevation in metres Used for elevation-corrected pressure calculations
Note on F2: SOURCES ONLY: Set pressure in kPa(g) Leave BLANK for junctions and offtakes Python converts: Pa(a) = value×1000 + 101325
Note on G2: OFFTAKES ONLY: Peak hourly demand (Sm³/h) Leave BLANK for sources Set to 0 for junctions
Note on H2: Dropdown: residential / commercial / industrial Determines default diversity factor range
Note on I2: 0.0 – 1.0 Residential: 0.50–0.70 Commercial: 0.80–0.95 Industrial: 1.00
Note on J2: FORMULA: = Demand × Diversity Factor =G*I This is the value passed to solver (D_u vector)
Note on K2: Minimum acceptable nodal pressure in kPa(g) Post-solve check: P_solved ≥ Min_P Residential: ≥7.5 kPa(g). Industrial: ≥50 kPa(g)
Note on L2: GIS X-coordinate (Easting) in metres Used for network map visualisation
Note on M2: GIS Y-coordinate (Northing) in metres Used for network map visualisation

## PIPES
GAS DISTRIBUTION NETWORK PIPE TABLE ¦ PE80 · 4 bar(g) · SI Units
Pipe_ID | From_Node | To_Node | Length_m | OD_mm | SDR | ID_mm | Material | Roughness_mm | Year_Install | Status | Length_m (Solver) | ID_m (Solver) | Rough_m (Solver) | PE80 SDR → MOP
P001 | N001 | N002 | 850 | 250 | 11 |  | PE80 |  | 2018 | open |  |  |  | SDR | MOP (bar) | Notes
P002 | N002 | N003 | 420 | 250 | 11 |  | PE80 |  | 2018 | open |  |  |  | SDR 11 | 4 | ★ This network
P003 | N002 | N004 | 380 | 250 | 11 |  | PE80 |  | 2017 | open |  |  |  | SDR 17 | 4.0
P004 | N003 | N005 | 400 | 180 | 11 |  | PE80 |  | 2019 | open
P005 | N003 | N006 | 290 | 180 | 11 |  | PE80 |  | 2019 | open
P006 | N004 | N007 | 260 | 110 | 11 |  | PE80 |  | 2020 | open
P007 | N004 | N008 | 440 | 63 | 11 |  | PE80 |  | 2020 | open
P008 | N009 | N004 | 1000 | 250 | 11 |  | PE80 |  | 2016 | open
P009 | N004 | N010 | 457 | 90 | 11 |  | PE80 |  | 2021 | open
Note on A2: Unique pipe identifier Format: P001, P002... Primary key
Note on B2: Starting node ID Must exactly match a Node_ID in NODES sheet Positive flow direction = From → To
Note on C2: Ending node ID Must exactly match a Node_ID in NODES sheet Solver corrects sign if flow is reversed
Note on D2: Physical pipe length in metres NOT straight-line distance Account for bends and route deviations Typically 1.05–1.15× straight-line
Note on E2: Pipe outside diameter in mm Standard PE80 sizes: 25·32·40·50·63·90·110·125·160·200·250·315
Note on F2: Standard Dimension Ratio = OD/WT PE80 at 4 bar → SDR17 (MOP=4bar) SDR11 (MOP=8bar), SDR21 (MOP=3bar)
Note on G2: FORMULA: Internal diameter in mm = OD × (1 - 2/SDR) Do NOT enter manually — always formula
Note on H2: Dropdown: PE80 / PE100 / Steel_new / Steel_aged / CI Determines roughness from MATERIALS sheet
Note on I2: FORMULA: from MATERIALS lookup = VLOOKUP(Material, MATERIALS, col, 0) Do NOT enter manually
Note on J2: Year pipe was installed Used for age-based condition assessment
Note on K2: Dropdown: open / closed / throttled Only 'open' pipes are passed to the solver Closed = valve isolated section
Note on L2: FORMULA: Length in metres for solver = D (same column, confirms unit)
Note on M2: FORMULA: ID in metres for solver = G/1000
Note on N2: FORMULA: Roughness in metres for solver = I/1000

## MATERIALS
MATERIAL REFERENCE TABLE ¦ Roughness values for Darcy-Weisbach / Swamee-Jain
Material | Roughness_mm | Roughness_m | MOP_bar | Standard | Notes
PE80 | 0.007 |  | 4 | ISO 4437 / EN 1555 | This network SDR11 @ 4 bar. Smooth bore.
PE100 | 0.007 |  | 10 | ISO 4437 / EN 1555 | Higher MRS, same roughness as PE80
Steel_new | 0.046 |  | 70 | ASME B31.8 | Commercial steel, new condition
Steel_aged | 0.1 |  | 70 | IGEM/TD/3 | Aged steel use after 20+ years service
Steel_coated | 0.02 |  | 70 | ISO 13623 | Internally coated steel transmission
CI | 0.25 |  | 3 | WIS 4-08-03 | Cast iron distribution legacy mains
GI | 0.15 |  | 3 | BS 534 | Galvanised iron
Ductile_CI | 0.05 |  | 10 | EN 545 | Ductile cast iron modern replacement
PE80 PIPE DIMENSIONS OD × SDR → ID (mm)
OD (mm) | SDR 11 ID (mm) | SDR 13.6 ID (mm) | SDR 17 ID (mm) | SDR 21 ID (mm) | SDR 26 ID (mm)
25 | 20.45 | 21.32 | 22.06 | 22.62 | 23.08
32 | 26.18 | 27.29 | 28.24 | 28.95 | 29.54
40 | 32.73 | 34.12 | 35.29 | 36.19 | 36.92
50 | 40.91 | 42.65 | 44.12 | 45.24 | 46.15
63 | 51.55 | 53.74 | 55.59 | 57 | 58.15
90 | 73.64 | 76.76 | 79.41 | 81.43 | 83.08
110 | 90 | 93.82 | 97.06 | 99.52 | 101.54
125 | 102.27 | 106.62 | 110.29 | 113.1 | 115.38
160 | 130.91 | 136.47 | 141.18 | 144.76 | 147.69
200 | 163.64 | 170.59 | 176.47 | 180.95 | 184.62
250 | 204.55 | 213.24 | 220.59 | 226.19 | 230.77
315 | 257.73 | 268.68 | 277.94 | 285 | 290.77

## VALIDATION
NETWORK VALIDATION CHECKS ¦ Run before executing solver ¦ All checks must show ✓ PASS
Check_ID | Description | Formula / Logic | Result | Status | Action if Fail
V01 | All pipe From_Nodes exist in NODES sheet |  |  |  | Check PIPES column B each From_Node must exactly match a Node_ID in NODES
V02 | All pipe To_Nodes exist in NODES sheet |  |  |  | Check PIPES column C each To_Node must exactly match a Node_ID in NODES
V03 | No duplicate Node_IDs |  |  |  | Duplicate Node_IDs found each node must have a unique ID
V04 | No duplicate Pipe_IDs |  |  |  | Duplicate Pipe_IDs found each pipe must have a unique ID
V05 | Source nodes have Known_P filled |  |  |  | Source node(s) missing Known_P fill F column for all source nodes
V06 | Source nodes have no Demand value |  |  |  | Source node(s) have demand > 0 sources supply gas, they do not consume it
V07 | Offtake nodes have Demand filled |  |  |  | Offtake node(s) missing Demand_Sm3h fill G column for all offtakes
V08 | Offtake nodes have no Known_P |  |  |  | Offtake node(s) have Known_P filled pressure is unknown for offtakes
V09 | All diversity factors are between 0 and 1 |  |  |  | Diversity factor out of range must be 0.0 to 1.0
V10 | All pipe lengths are positive |  |  |  | Pipe(s) with zero or negative length check PIPES column D
V11 | All pipe diameters are positive |  |  |  | Pipe(s) with zero or negative OD check PIPES column E
V12 | SDR values are valid (11–26 range) |  |  |  | Invalid SDR value PE80 standard SDRs: 11, 13.6, 17, 21, 26
V13 | No roughness errors in PIPES (VLOOKUP working) |  |  |  | Material not found in MATERIALS table check spelling in PIPES column H
V14 | At least one source node exists |  |  |  | No source node defined add at least one PRS or PRV as a source node
V15 | At least one offtake node exists |  |  |  | No offtake node defined add customer meter stations as offtake nodes
V16 | Total number of nodes |  |  |  | Information only verify matches your network sketch
V17 | Total number of pipes (open only) |  |  |  | Information only closed/throttled pipes excluded from solver
V18 | Total effective demand (Sm³/h) |  |  |  | Verify this is plausible for your network size and customer mix
V19 | Pipe-to-node ratio (should be ≥ 1 for looped network) |  |  |  | Ratio < 1 means purely radial network no redundancy. Add loop pipes if required.
V20 | Overall PASS / FAIL |  |  |  | Fix all FAIL checks before passing data to the Python solver

## RESULTS
PE80 GAS NETWORK — SOLVER RESULTS ¦ CONVERGED ¦ 18 iterations ¦ max¦F¦ = 6.562e-07 Sm³/s
NODE RESULTS
Node_ID | Label | Type | Solved_P [kPa(g)] | Min_P [kPa(g)] | Margin [kPa] | Status
N001 | PRS1 | source | 400 | 0 | 400 | SOURCE (fixed P)
N002 | TEE1 | junction | 399.06 | 0 | 399.06 | [OK] (399.1 kPa margin)
N003 | TEE2 | junction | 398.52 | 0 | 398.52 | [OK] (398.5 kPa margin)
N004 | TEE3 | junction | 399.07 | 0 | 399.07 | [OK] (399.1 kPa margin)
N005 | Client1 | offtake | 397.6 | 390 | 7.6 | [!] LOW MARGIN (7.6 kPa)
N006 | Client2 | offtake | 398.12 | 390 | 8.12 | [!] LOW MARGIN (8.1 kPa)
N007 | Client3 | offtake | 397.23 | 390 | 7.23 | [!] LOW MARGIN (7.2 kPa)
N008 | Client4 | offtake | 327.34 | 390 | -62.66 | [FAIL] BELOW MIN by 62.7 kPa
N009 | PRS2 | source | 400 | 0 | 400 | SOURCE (fixed P)
N010 | Client5 | offtake | 397.3 | 390 | 7.3 | [!] LOW MARGIN (7.3 kPa)
PIPE RESULTS
Pipe_ID | From | To | Q [Sm³/h] | Direction | v [m/s] | Re [-] | f [-] | ΔP [mbar] | Grad [mbar/m] | Loading [%] | Status
P001 | N001 | N002 | 1601.084 | -> | 2.7472 | 190608 | 0.01598 | 9.357 | 0.01101 | 4.36 | [OK]
P002 | N002 | N003 | 1750 | -> | 3.0072 | 208336 | 0.015726 | 5.444 | 0.01296 | 4.77 | [OK]
P003 | N002 | N004 | -148.917 | <- | 0.2558 | 17728 | 0.026695 | -0.061 | 0.00016 | 0.41 | [REV] REVERSED
P004 | N003 | N005 | 1000 | -> | 3.3197 | 165346 | 0.016506 | 9.197 | 0.02299 | 5.26 | [OK]
P005 | N003 | N006 | 750 | -> | 2.4884 | 124010 | 0.01741 | 3.954 | 0.01363 | 3.94 | [OK]
P006 | N004 | N007 | 500 | -> | 4.4437 | 135283 | 0.017334 | 18.41 | 0.07081 | 7.04 | [OK]
P007 | N004 | N008 | 599.998 | -> | 17.4795 | 283450 | 0.015882 | 717.266 | 1.6301 | 26.69 | [!] HIGH GRAD
P008 | N009 | N004 | 1458.916 | -> | 2.5033 | 173683 | 0.016253 | 9.297 | 0.0093 | 3.97 | [OK]
P009 | N004 | N010 | 210 | -> | 2.7878 | 69445 | 0.019766 | 17.752 | 0.03885 | 4.42 | [OK]
MASS BALANCE |  |  |  | Total supply [Sm³/h] | 3060 | Total demand [Sm³/h] | 3060 | Balance [Sm³/h] | 0